## Sheet1
Jignesh.Parmar www.electricalnotes.wordpress.com jiguparmar@yahoo.com
TOUCH VOLTAGE & GROUND CURRENT CALCULATION
Three Phase System |  |  |  | Single Phase System
| Line-to-Neutral Volts (Vn) | 230 | Volts |  | Circuit Voltage | 230 | Volts
| Line 1 Calculated Load (A1) | 50 | Amp |  | Circuit Ampere | 16 | Amp
| Line 2 Calculated Load (A2) | 60 | Amp |  | Load Resistance | 14.375 | Ω
| Line 3 Calculated Load (A3) | 60 | Amp
| Service Neutral Impedance Z1 | 0.1 | Ω |  | Ground Resistance | 1 | Ω
| Ground Resistance (3-point method) R | 100 | Ω |  | Electrode Resistance | 25 | Ω
[5 empty] | Body Resistance | 1000 | Ω
| RESULTS |  |  |  | RESULTS
| Neutral/Ground Parallel Resistance | 0.0999 | Ω |  | Total Resistance | 38.7652 | Ω
| Line 1 Resistance | 4.6 | Ω |  | Total Current | 5.9331 | Amp
| Line 2 Resistance | 3.8333 | Ω |  | Load Voltage Drop | 85.289 | Volts
| Line 3 Resistance | 3.8333 | Ω
2331.9141
47.0331
| Line 1 - Actual Load | 49.5802 | Amp
| Line 1 Watts | 11307.7198 | Watts |  | Ground/Body Voltage Drop | 144.711 | Volts
| Line 1 - Loads Operates at Volts | 228.0691 | Volts |  | Body Resistance | 1000 | Ω
[5 empty] | Body Current | 144.711 | mA
| Line 2 - Actual Load | 59.7353 | Amp |  | Circuit Current | 14.9593 | Amp
| Line 2 Watts | 13678.5289 | Watts
| Line 2 - Loads Operates at Volts | 228.9855 | Volts
| Line 3 - Actual Load | 59.7353 | Amp
| Line 3 Watts | 13678.5289 | Watts
| Line 3 - Loads Operates at Volts | 228.9855 | Volts
| Parallel Neutral/Ground Path | 69.8905 | Amp
| Neutral Watts | 487.9797 | Watt
| Neutral Current | 69.8206 | Amp
| Ground Current | 0.069821 | Amp
| Touch Voltage from Metal Parts to Earth | 6.9821 | Volts